QTR-SB-01 — Serra Branca Solar Plant: Quarterly O&M Service Report (Q3 2025)

Document ID: QTR-SB-01
Document type: Quarterly service performance report
Reporting period: 2025-07-01 to 2025-09-30 (Q3 2025)
Prepared by: Solaria Delta Services, S.A. (“SDG Services”)
Prepared for: Serra Branca Solar, S.A. (“Plant Owner”)
Site: Serra Branca Solar Plant (“Serra Branca”)
Issue date: 2025-10-10
Version: v1.0

1. Executive Summary

During Q3 2025, SDG Services delivered routine operations support and maintenance services for Serra Branca in accordance with the O&M Agreement. Activities focused on preventive inspections, corrective maintenance response, vegetation control coordination, inverter servicing, and monthly reporting.

Scope note: This quarterly report covers service delivery and O&M performance. It does not cover electricity sales, trading, market settlement, or revenue. Commercial offtake arrangements and electricity sales remain the responsibility of the Plant Owner (or the Owner’s appointed commercial representative).

2. Service Performance KPIs (Q3 2025)

KPI-1: Technical availability (plant level)

- Target: ≥ 98.0%

- Actual (Q3 2025): 98.6%

KPI-2: Response time for critical incidents

- Target: on-site within 8 hours

- Actual (Q3 2025): 100% within target (3/3 incidents)

KPI-3: Mean time to repair (MTTR) — critical incidents

- Target: ≤ 48 hours

- Actual (Q3 2025): 31 hours average

KPI-4: Preventive maintenance completion

- Target: 100% of planned PM tasks completed within quarter

- Actual (Q3 2025): 100% completed

3. Work Performed (Summary)

3.1 Preventive Maintenance (PM)

- Monthly inverter inspections and cleaning checks (all inverter stations)

- Thermographic survey of selected DC strings (spot checks per plan)

- Torque verification on critical electrical connections (sample basis)

- Visual inspection of module rows for hotspots and mechanical damage

- SCADA alarm review and parameter sanity checks

- Spare parts inventory reconciliation and reorder recommendations

3.2 Corrective Maintenance (CM)

CM-01 (2025-07-18): Inverter station fault — fan assembly replacement

- Action: replaced fan assembly, validated cooling performance

- Downtime: 6.5 hours

- Root cause: wear component failure

CM-02 (2025-08-21): String-level underperformance alarm

- Action: inspected combiner box, replaced blown fuse, verified string recovery

- Downtime: 4.0 hours

- Root cause: fuse failure

CM-03 (2025-09-09): SCADA communications intermittent

- Action: network switch replacement + configuration verification

- Downtime: 2.0 hours

- Root cause: switch hardware failure

4. Health, Safety, and Environmental (HSE) Notes

- No lost-time incidents recorded in the reporting period.

- Routine HSE briefings conducted prior to on-site work orders.

- Waste from replaced electrical components handled through approved disposal channels per site procedures (records held by SDG Services; not reproduced here).

5. Exceptions / Exclusions

The following items are outside SDG Services’ contractual responsibilities unless separately agreed in writing:

- Electricity trading, power purchase agreements, market bidding, settlement, invoicing for electricity sales

- Permit-holder obligations and operator-of-record responsibilities

- Major refurbishment / repowering works (beyond routine O&M)

Prepared by:
Name: Ricardo Iglesias
Role: O&M Manager, SDG Services
Signature: Ricardo Iglesias
Date: 2025-10-15