QTR-RF-01 — Ribeira Flex: Quarterly Technical Operations & Asset Inventory Report (Q3 2025)

Document ID: QTR-RF-01
Document type: Quarterly technical operations & inventory report
Reporting period: 2025-07-01 to 2025-09-30 (Q3 2025)
Issue date: 2025-10-12
Version: v1.0
Prepared by: SDG Technical Operations (Flex Assets)
Asset: Ribeira Flex (“RF”)
Location: Portugal (site identifiers withheld in distributed pack)

1. Executive Summary

During Q3 2025, an in-depth preventive maintenance campaign and asset inventory verification was performed for Ribeira Flex. The campaign included inspection of primary power conversion equipment, battery racks, protection systems, metering configuration, and control/dispatch interfaces.

Asset type: Battery Energy Storage System (BESS) providing grid-connected flexibility through controlled charging (import) and discharging (export) operations.

2. Technical Overview (as operated)

2.1 Rated Capacity (Nameplate)

| Parameter | Value |
| --- | --- |
| Rated power (AC) | 20 MW |
| Energy capacity (usable) | 40 MWh |
| Technology | Lithium-ion BESS with Power Conversion System (PCS) |
| Grid connection | Medium-voltage connection at Point of Common Coupling (PCC) |

2.2 Functional Description

Ribeira Flex operates as a grid-connected storage asset that:

- charges from the grid (import) when instructed by dispatch/control signals or when operating schedules require charging; and

- discharges to the grid (export) to provide flexibility services and energy delivery when instructed.

3. Full Equipment Inventory (verified Q3 2025)

| Equipment category | Verified components (examples) | Quantity / notes |
| --- | --- | --- |
| Battery subsystem | Battery racks (containerised), Battery Management System (BMS) | 10 containers; BMS verified |
| Power Conversion System | Bidirectional PCS units (AC/DC) | 10 PCS skids |
| Protection & switchgear | MV switchgear, protection relays, isolators | Verified functional tests |
| Auxiliary systems | HVAC (container cooling), fire detection/suppression | All containers equipped |
| Control systems | SCADA interface, dispatch/control gateway | Signal integrity check completed |
| Transformer package | Step-up transformer for grid interconnection | Nameplate confirmed |

4. Metering Configuration Summary (verified)

Ribeira Flex metering is configured for bidirectional energy flows consistent with charging and discharging operations.

| Metering item | Configuration | Operational implication |
| --- | --- | --- |
| Import (charging) measurement | Energy imported from grid measured for charging events | Confirms grid-to-storage charging |
| Export (discharging) measurement | Energy exported to grid measured for discharging events | Confirms storage-to-grid delivery |
| Operational logs | Charge/discharge events recorded in SCADA | Supports dispatchable storage operation |

5. Operations KPIs (Q3 2025)

| KPI | Target | Actual (Q3 2025) |
| --- | --- | --- |
| Availability (storage capability) | ≥ 98.0% | 98.4% |
| Dispatch compliance (event execution) | ≥ 99.0% | 99.2% |
| Mean time to respond (critical alarm) | ≤ 2 hours | 1.4 hours |
| Preventive maintenance completion | 100% | 100% |

6. Maintenance Highlights (Q3 2025)

- PCS firmware verification and parameter checks completed.

- Battery container thermal management review completed; HVAC performance within operating thresholds.

- Fire detection and suppression systems tested (sample-based).

- Dispatch/control gateway signal integrity test completed (no anomalies).

- Protection relay settings review performed (no changes required).

Prepared by:
Name: Paulo Monteiro
Role: Technical Operations Lead (Flex Assets)
Signature: Paulo Monteiro
Date: 09.10.2025